## Slide 1: Rep Training
AK Series Product Training

## Slide 2: PRAK Series
PRRA
PRAK
PREK
575V Not Available

## Slide 3: AK Series
Compact Footprint series
3 – 90 Tons
400 to 19,000 CFM
EC Fan motor
2” Foam Injected Cabinet
Bitzer Scrolls – Optional Lead VFD Option
Condensing fans: axial sickle shaped w/ VFD
Gas furnace max 1200 MBH
Electric heat max 150 kW
-20 °F winter design
PRAK – 100% OA, air cooled
PREK – 100% OA, air cooled with enthalpy wheel
PRRK – recirc / mixed air, air cooled (opt. enthalpy wheel)

## Slide 4: AK Series

## Slide 5: AK Series
Air Cooled
Liquid Sub Cool and HGRC standard for 100% OA
  PRAK & PREK
  PRRK offers Modulating HGRC
Smaller footprint over PR**
Less weight over PR**
MAY be less cost than PR*A

## Slide 6: PRAK Series

## Slide 7: AK Series, Base
“C” Channel, 12 ga. G-90 steel
Bolted construction
Cabinet: S3 and S5
6” base rail

## Slide 8: AK Series, Base
Tubular structural steel
Welded construction
Cabinet: S7 ( without ECW Wheel)
4” base rail
Cabinet: S7 ( with ECW Wheel)
6” base rail

## Slide 9: AK Series, Filter
Galvanized steel track
2” + 4”
All prefilter location
Magnehelic gauge, local read only
Clogged filter switch, BMS alarm

## Slide 10
Energy Recovery Wheels, PREK & PRRK
Poylmer wheel, segmented, with silica gel desiccant
ADD Option: Aluminum substrate, single piece, with 3A (angstrom) molecular sieve desiccant
Purge feature
Bearings L-10; 30 years maintenance free
Slide out cassette for ease of cleaning and maintenance

## Slide 11: EK and RK Series Unit
ADD Option: Energy Wheel with Exhaust Fan:
Available from 3 - 70 Ton cabinet size
Exhaust fans located in ‘bump out’
LH and RH access w/ RH for ‘pull’ to remove enthalpy wheel

## Slide 12
AK Series, EC Fan Motor
575V not available, today
Ziehl Abegg, EBM Papst, Rosenberg
Check your ACE selection for fan quantity and specification opportunity

## Slide 13: PRAK Series

## Slide 14
PR_K, 3 - 10 Tons, S1
Code string PR_K118S1
Mitsubishi inverter compressor:
PRAK118S1 dx LAT high at 200cfm/ton
PRRK, PREK ‘manageable’ with lower EAT with the help mixed air or wheel
Is a lower first cost than PR_K120S3

## Slide 15
Code string PR_K118S1
150MBH Gas Heat:
Maximum output from factory
Cold weather regions: ASHRAE zone 5,6,&7 and Canada
Supplemental duct furnace ?
Is a lower first cost than PR_K120S3

## Slide 16
PRRK118S1, Base: $35000 ~ $3.5 k/ton
PRRK120S3, Base: $55,000K ~ $5.5 k/ton

## Slide 17
AK-1 vs. Competition

## Slide 18
AK-1 vs. Competition

## Slide 19: PRAK Series Capabilities and Dimensions

## Slide 20: PRRA Recirculation with Exhaust fan or w/o exh fan

## Slide 21: PRRA Recirculation with Exhaust Fan
Real Basic $52K ~$2.9k/ton
Real Basic $58K ~$2.9k/ton

## Slide 22: PRRA Mixed Outside air ( 3-70 tons)
2 Cabinet Sizes S5 and S7
  Replacement for Legacy PCA/DCA Footprints
  Replacement for Other MFGs Footprints
  Adapter curbs can be used for most applications
20 – 90 Tons
5000 to 19,00 CFM
Prak 3-90tons
PRRK 3-70 ton
PREK 3 -70 ton

## Slide 23: FAQ
Special Tracker items not reviewed in preso
oA intake and ea discharge on same end – cross contam
Show plan dwg where elect serviced is introduced but where disc might be though

## Slide 24: PROA vs PRAK

## Slide 25: PROA vs PRAK Airflow Cabinets
Notes: Why are some of my selections favoring the PROA vs the PRAK?
The PRAK was designed with an emphasis on a more compact footprint.
The PROA will have more options and applied specials available.
In some cases, the PROA will be less expensive especially if you are in the upper box size and the PRAK is in the lower box size.
In certain applications, the PROA model might be the better choice.
The key is you can use both the PROA and PRAK Series to bid all jobs.

## Slide 26: PR SERIES Capabilities & Dimensions
In the PR code string, an “XL” means cabinet extension for heat : electric KW or gas – dual /quad. This equates to an increase in cabinet cost and provides a signal to price check with an AK unit

## Slide 27: PROA vs PRAK SIZE
PROA |  |  |  | PRAK | PRAK |  | 
Cabinet | Length | Width | Height | Cabinet | Length | Width | Height
A | 137 | 61 | 55 | 1 | 99 | 51 | 77
B | 170 | 87 | 92 | 3 | 115 | 80 | 77
C | 185 | 87 | 92 | 5 | 152 | 85 | 98
D | 264 | 87 | 92 | 7 | 202 | 100 | 110
E | 330 | 100 | 108 | 9 |  |  | 
AK smaller footprint over PR – freight costs
AK Less weight over PR – design and structural

## Slide 28
Each units is tested

## Slide 29: THANK YOU